## EBA
Electric Bill Analysis
Name : | Location Name
Address:
City: |  |  |  | State:
ZIP: |  |  |  | Country:
Service Voltage: |  | Phase: |  | Amperage:
* Month | Kwh's Used | Demand | Billing | Monthly Cost | Cost per Kwh | Load
|  | Kw or Kva | Days |  |  | Factor
2004-08-01 | 83149 | 374 | 27 | 7063.57 | 0.084951 | 34.31%
2004-07-01 | 98286 | 365 | 31 | 7254.4 | 0.073809 | 36.19%
2004-06-01 | 106164 | 367 | 33 | 7686.35 | 0.072401 | 36.52%
2004-05-01 | 76576 | 352 | 29 | 6017.16 | 0.078578 | 31.26%
2004-04-01 | 72405 | 352 | 32 | 5985.63 | 0.082669 | 26.78%
2004-03-01 | 57998 | 352 | 28 | 5452.39 | 0.09401 | 24.52%
2004-02-01 | 64676 | 352 | 30 | 5638.07 | 0.087174 | 25.52%
2004-01-01 | 66149 | 352 | 30 | 5893.88 | 0.0891 | 26.1%
2003-12-01 | 65665 | 352 | 34 | 5787.84 | 0.088142 | 22.86%
2003-11-01 | 61693 | 351 | 29 | 5820.89 | 0.094353 | 25.25%
2003-10-01 | 65337 | 351 | 28 | 5787.58 | 0.08858 | 27.7%
2003-09-01 | 101753 | 360 | 33 | 7327.08 | 0.072008 | 35.69%
Annual Total: | 919851 | 4280 | 364 | 75714.84 | NA | NA
Mthly Average: | 76654.25 | 356.6667 | 30.3333 | 6309.57 | 0.083815 | 0.29392
Business Hours | Sun | Mon | Tue | Wed | Thur | Fri | Sat
| 10 | 8 | 10 | 10 | 10 | 10 | 10
Total Hrs per week: |  | 68 |  | Climate: | Temperate
Exchange Rate: |  | 1 |  | Facility Type: | Country Club
Currency: |  | $
Hertz: |  | 60
Last Name: | thompson |  |  | First name: | glendon
Company Name: | Arcom Group, Inc.
Phone#: | (770) 971-6778 |  |  | e-mail: | glendont@bellsouth.net
Address: | 4205 Parnell Road
City: | Marietta |  |  | State: | Georgia
ZIP: | 30062 |  |  | Country: | USA

## Fluorescent
Fluorescent Lights
No. | Location | Fix. Qty | Bulb Length | Bulbs Per Fixture | Watts | Bulb Type | Ballast Type | W/P | Volts | Months | H/W
1 | Top Level 3 | 1 | 4 | 4 | 34 | T12 | Magnetic | Wall | 120 | 12 | 50
2 | TOP LEVEL 2 | 1 | 4 | 4 | 34 | T12 | Magnetic | Wall | 120 | 12 | 50
3 | TOP LEVEL 1 | 1 | 4 | 4 | 34 | T12 | Magnetic | Wall | 120 | 12 | 50
4 | TOP LEVEL 4 | 2 | 4 | 4 | 34 | T12 | Magnetic | Wall | 120 | 12 | 50
5 | GF KITCHEN | 7 | 4 | 4 | 34 | T12 | Magnetic | Wall | 120 | 12 | 50
6 | GF KITCHEN | 2 | 4 | 2 | 34 | T12 | Magnetic | Wall | 120 | 12 | 50
7 | GF KITCHEN | 3 | 8 | 2 | 60 | T12 | Magnetic | Wall | 120 | 12 | 50
8 | GF STORAGE | 1 | 8 | 2 | 60 | T12 | Magnetic | Wall | 120 | 12 | 50
9 | GF SERVICE HALL | 2 | 8 | 2 | 60 | T12 | Magnetic | Wall | 120 | 12 | 50
10 | GF LIQUOR ROOM | 1 | 4 | 2 | 34 | T12 | Magnetic | Wall | 120 | 12 | 50
11 | B HALL | 4 | 4 | 4 | 34 | T12 | Magnetic | Wall | 120 | 12 | 50
12 | B HALL | 6 | 4 | 2 | 32 | U-Shape | Electronic | Wall | 120 | 12 | 50
13 | B BREAK ROOM | 2 | 4 | 4 | 34 | T12 | Magnetic | Wall | 120 | 12 | 50
14 | B MEN'S LOCKERS | 25 | 4 | 2 | 32 | U-Shape | Electronic | Wall | 120 | 12 | 50
15 | B STORAGE 1 | 8 | 8 | 2 | 60 | T12 | Magnetic | Wall | 120 | 12 | 50
16 | B STORAGE 2 | 1 | 4 | 4 | 34 | T12 | Magnetic | Wall | 120 | 12 | 50
17 | B STORAGE 2 | 1 | 4 | 2 | 34 | T12 | Magnetic | Wall | 120 | 12 | 50
18 | B STORAGE 3 | 3 | 8 | 2 | 60 | T12 | Magnetic | Wall | 120 | 12 | 50
19 | B PROSHOP OFFICE 1 | 2 | 4 | 4 | 34 | T12 | Magnetic | Wall | 120 | 12 | 50
20 | B PROSHOP OFFICE 2 | 2 | 4 | 4 | 34 | T12 | Magnetic | Wall | 120 | 12 | 50
21 | B LADIES LOUNGE | 19 | 4 | 2 | 32 | U-Shape | Electronic | Wall | 120 | 12 | 50
22 | B LADIES LOUNGE | 9 | 4 | 2 | 32 | U-Shape | Electronic | Wall | 120 | 12 | 50
23 | B FITNESS CENTER | 18 | 4 | 3 | 32 | T8 | Electronic | Wall | 120 | 12 | 50
24 | SB CART SERVICE OFFICE | 2 | 8 | 2 | 60 | T8 | Electronic | Wall | 120 | 12 | 50
25 | SB CLUB STORAGE | 12 | 8 | 2 | 34 | T8 | Magnetic | Wall | 120 | 12 | 50
26 | SB CLUB STORAGE | 5 | 4 | 2 | 34 | T8 | Magnetic | Wall | 120 | 12 | 50
27 | SB CLUB STORAGE | 6 | 8 | 2 | 60 | T8 | Magnetic | Wall | 120 | 12 | 50
28 | SB CART STORAGE | 15 | 8 | 2 | 60 | T12 | Magnetic | Wall | 120 | 12 | 50
29 | SB SHOP | 2 | 8 | 2 | 60 | T12 | Magnetic | Wall | 120 | 12 | 50
30 | SB BATH | 1 | 4 | 2 | 32 | U-Shape | Magnetic | Wall | 120 | 12 | 50
31 | MAINTENANCE BLDG | 18 | 8 | 2 | 60 | T8 | Magnetic | Wall | 120 | 12 | 50
32 | MAINTENANCE BLDG | 9 | 4 | 2 | 34 | T8 | Magnetic | Wall | 120 | 12 | 50
33 | MAINTENANCE BLDG | 2 | 4 | 4 | 34 | T8 | Magnetic | Wall | 120 | 12 | 50
34 | POOL MAINTENANCE BLDG | 4 | 4 | 2 | 34 | T8 | Magnetic | Wall | 120 | 8 | 50
35
36
Note on C2: Fixture Quantity

## Subpanel
Subpanel
Row | M, P |  |  |  |  | Rated |  | Upstream source | Distance from
No | or T | Number | Location | V in | V out | Amps | Connection | From P# or T# | Upstream source
1 | Panel | LQ | main club house GOLF SHOP | 208/120 |  | 200 | 3Ph-Delta | CY6196 | 40 FEET
2 | Panel | LF | main club house LOCKER ROOM | 208/120 |  | 200 | 3Ph-Delta | CY6196 | 40
3 | Panel | LI | MAIN CLUB HOUSE FITNESS CENTER | 208/120 |  | 200 | 3Ph-Delta | CY6196 | 70 FEET
4 | Panel | D13E4622 | MAIN CLUB HOUSE BAG ROOM | 208/120 |  | 125 | 3Ph-Delta | CY6196 | 100
5 | Meter | CY6196 | main club house | 240/120 |  | 1600 | 3Ph-Delta
6 | Panel | C1J1991/R1 | main club house cart barn battery chargers | 240/120 |  | 150 | 3Ph-Delta
7 | Panel | R2 | MAIN CLUB HOUSE CART BARN | 240/120 |  | 200 | 3Ph-Delta | CY6196 | 120 FEET
8 | Panel | Q0 | MAIN CLUB HOUSE CART BARN | 240/120 |  | 100 | 1Ph Single | CY6196 | 120 FEET
9 | Panel | GE LEFT | MAIN CLUB HOUSE OUTSIDE CART BARN | 208/120 |  | 150 | 3Ph-Delta | CY6196 | 130
10 | Panel | GE RIGHT | MAIN CLUB HOUSE OUTSIDE CART BARN | 208/120 |  | 150 | 3Ph-Delta | CY6196 | 130 FEET
11 | Panel | LD2 | MAIN CLUB HOUSE NEXT TO KITCHEN | 208/120 |  | 150 | 3Ph-Delta | CY6196 | 25 FEET
12 | Panel | LD3 | MAIN CLUBHOUSE NEXT TO KITCHEN | 208/120 |  | 300 | 3Ph-Delta | CY6196 | 25 FEET
13 | Panel | LD | MAIN CLUB HOUSE NEXT TO KITCHEN | 208/120 |  | 200 | 3Ph-Delta | CY6196 | 25
14 | Panel | LD4 | MAIN CLUB HOUSE NEXT TO KITCHEN | 208/120 |  | 150 | 3Ph-Delta | CY6196 | 25
15 | Panel | LD5 | MAIN CLUB HOUSE NEXT TO SERVICE DOOR | 240/120 |  | 200 | 3Ph-Delta | CY6196 | 30
16 | Panel | LD6 | MAIN CLUB HOUSE NEXT T SERVICE DOOR | 240/120 |  | 250 | 3Ph-Delta-Gnd | CY6196 | 40 FEET
17 | Panel | LJ | MAIN CLUB HOUSE DINING ROOM | 240/120 |  | 200 | 3Ph-Delta | CY6196 | 50 FEET
18 | Meter | BC5054 | MAINTENANCE SHOP | 240/120 |  | 200 | 1Ph Single
19 | Panel | M1 | OFFICE END OF MAINTENANCE SHOP | 240/120 |  | 200 | 1Ph Single | BC5054 | 30 FEET
20 | Panel | M2 | MECHANICAL END OF MAINTENANCE SHOP | 240/120 |  | 150 | 1Ph Single | BC5054 | 150 FEET
21 | Meter | BD9493 | RIGHT OF MAIN BLDG - IRRIGATION | 480 |  | 150 | 3Ph-Wye
22 | Meter | MM6685 | 11TH GREEN - NO LOAD ATTACHED | 240/120 |  | 200 | 3Ph-Wye
23 | Meter | CB4496 | MAIN PUMPING STATION HOUSE | 240/120 |  | 200 | 3Ph-Wye
24 | Meter | K46776 | 17TH TEE-NO LOAD ATTACHED | 240/120 |  | 200 | 3Ph-Wye
25 | Meter | CJ2292 | 3RD TEE-NO LOAD ATTACHED | 240/120 |  | 200 | 3Ph-Wye
26 | Panel | P1 | INSIDE POOL UTIL ROOM | 240/120 |  | 200 | 3Ph-Delta | BJ1356 | 80 FEET
27 | Meter | CJ7928 | TENNIS CLAY COURTS | 240/120 |  | 200 | 1Ph Single
28 | Panel | BESIDEMETER | BESIDE CLAY COURT METER | 240/120 |  | 200 | 1Ph Single | CJ7928 | 5 FEET
29 | Meter | AB5419 | TENNIS CENTER HUT | 240/120 |  | 200 | 1Ph Single
30 | Panel | TC1 | TENNIS CENTER HUT | 240/120 |  | 200 | 1Ph Single | AB5419 | 5 FEET
31 | Meter | BJ1356 | OVERLOOKING POOL AT PARKING LOT TRANSFORMER | 120 |  | 400 | 3Ph-Delta
32 | Panel | HO7E2 | MAIN PUMPING STATION | 240/120 |  | 200 | 3Ph-Wye | CB4496 | 5 FEET
33

## Equipment
Equipment
[6 empty] | HP or |  |  | Total |  | Enclosure | branch | Wire | Wires/ | From |  | Actual Measurements
No | Eq. Description | Qty | Volts | Amp | Ph | KW | H/W | Type | HP | Mth | Type | ckt Lth | Size | Phase | Panel # | Volts | Amps | KW | PF | KVAR | %THD/I-F
1 | mAINTENANCE BLDG GOLF CART LIFT | 1 | 208 | 0 | 1 | 2 | 1 | NoTreat | 2 | 12 | Indoors
2 | MAINTENANCE BLDG REEL GRINDER | 1 | 220 | 9 | 1 | 1.5 | 1 | NoTreat | 1.5 | 12 | Indoors
3 | MAINTENANCE BLDG BED KNIFE GRINDER | 1 | 220 | 9 | 1 | 1.5 | 3 | NoTreat | 1.5 | 12 | Indoors
4 | MAINTENANCE BLDG AIR COMPRESSOR | 1 | 120 | 0 | 1 | 0 | 0 | NoTreat | 0 | 12 | Indoors
5 | MAINTENANCE BLDG WELDER 1 | 1 | 220 | 180 | 1 | 33.7 | 0.5 | NoTreat | 33.7 | 12 | Indoors
6 | MAINTENANCE BLDG WELDER 2 | 1 | 220 | 130 | 1 | 24.3 | 0.5 | NoTreat | 24.3 | 12 | Indoors
7 | MAINTENANCE BLDG HOIST | 1 | 220 | 16 | 1 | 3 | 0.5 | NoTreat | 3 | 12 | Indoors
8 | MAINTENANCE BLDG ICE MACHINE | 1 | 120 | 13.2 | 1 | 1.3 | 50 | Standard | 1.3 | 12 | Indoors
9 | MAINTENANCE BLDG BATTERY CHARGER | 4 | 120 | 12 | 1 | 1.2 | 50 | Battery Charger | 4.8 | 12 | Indoors
10 | MAINTENANCE BLDG BATTERY CHARGER | 1 | 120 | 10 | 1 | 1 | 50 | Battery Charger | 1 | 12 | Indoors
11 | MAINTENANCE BLDG SMALL FRIDGE | 2 | 120 | 1.4 | 1 | 0.1 | 50 | NoTreat | 0.2 | 12 | Indoors
12 | MAINTENANCE BLDG WINDOW AC UNIT | 2 | 120 | 1.5 | 1 | 0.2 | 50 | NoTreat | 0.4 | 8 | Indoors
13 | CART BARN BATTERY CHARGERS(WATT-MISER) | 68 | 120 | 9 | 1 | 0.9 | 50 | NoTreat | 61.2 | 12 | Indoors
14 | PRO SHOP AIR COMPRESSOR | 1 | 120 | 15 | 1 | 1.5 | 20 | NoTreat | 1.5 | 12 | Indoors
15 | POOLMUSHROOM PUMP | 1 | 208 | 21 | 1 | 5 | 24 | Standard | 5 | 5 | Indoors
16 | POOL PUMP MAIN FILTER | 1 | 230 | 7.1 | 1 | 0.75 | 50 | Standard | 0.8 | 5 | Indoors
17 | POOL ICE MACHINE | 1 | 120 | 2 | 1 | 0.2 | 50 | NoTreat | 0.2 | 5 | Indoors
18 | POOL SODA COOLERS | 2 | 120 | 2 | 1 | 0.2 | 50 | NoTreat | 0.4 | 5 | Indoors
19 | POOL PUMP AT PUMP HOUSE | 1 | 120 | 40 | 3 | 7.1 | 50 | Wye-Delta | 7.1 | 5 | Indoors
20 | MAIN PUMP HOUSE PUMP1(LEFT) | 1 | 230 | 128 | 3 | 50 | 16 | Wye-Delta | 50 | 12 | Indoors
21 | KITCHEN ICE MACHINE | 1 | 120 | 6 | 1 | 0.6 | 50 | Standard | 0.6 | 12 | Indoors
22 | MAIN PUMP HOUSE PUMP2(CENTER) | 1 | 230 | 65 | 3 | 25 | 16 | Wye-Delta | 25 | 12 | Indoors
23 | MAIN PUMP HOUSE PUMP3(RIGHT) | 1 | 230 | 128 | 3 | 50 | 16 | Wye-Delta | 50 | 12 | Indoors
24 | MAIN PUMP HOUSE BUTTERFLY VALVE | 3 | 120 | 0.65 | 3 | 0.1 | 16 | Wye-Delta | 0.3 | 12 | Indoors
25 | MAIN PUMP HOUSE EXHAUST FAN | 1 | 120 | 1.4 | 1 | 0.1 | 168 | Standard | 0.1 | 12 | Indoors
26
27
28

## Resistive
Resistive
No. | Load Description | Qty | Volts | Amps | Wattage | Month | H/W
1 | COMPUTERS ALL LOCATIONS | 15 | 120 | 3 | 5400 | 12 | 50
2 | MICROWAVE UNITS - MAINT BLDG | 2 | 120 | 12.4 | 2976 | 12 | 10
3 | COMPUTER PRINTERS | 7 | 120 | 1.4 | 1176 | 12 | 10
4 | MAIN PRINTER/COPIER | 1 | 120 | 12 | 1440 | 12 | 10
5 | STEAMER IN KITCHEN | 1 | 220 | 25 | 9000 | 12 | 10
6 | GLASS WASHER IN KITCHEN | 1 | 120 | 20 | 2400 | 12 | 12
7 | 48" TV IN BAR | 1 | 115 | 3 | 345 | 12 | 50
8 | 20" TELEVISIONS | 11 | 115 | 2 | 2530 | 12 | 50
9 | CART BARN LARGE HOT WATER HEATER | 1 | 115 | 5 | 575 | 12 | 50
10 | CART BARN SMALL HOT WATER HEATER | 1 | 240 | 3 | 720 | 12 | 50
11 | CART BARN WASHING MACHINE | 1 | 115 | 1.5 | 172.5 | 12 | 12
12 | CART BARN DRYERS | 2 | 220 | 12 | 5280 | 12 | 12
13 | POOL MEDIUM HOT WATER HEATER | 1 | 208 | 125 | 45000 | 6 | 50
14 | MAINTENANCE BARN SMALL HOT WATER HEATER | 1 | 240 | 3 | 720 | 12 | 50
15

## AirConditioning
Air Conditioning
No |  |  |  |  | Nameplate Data |  |  |  | Mechanical Data |  |  | Months |  | Total |  | Measured Data
| Location | Qty | Item | Volts | RLA | LRA | Ph | HP | Refrigerant | Line Size | H/W | start | end | HP | Volts | Amps | KW | KVAR | %THD/I-F
1 | maintenance window unit | 2 | Self-Contained | 115 | 4.5 | 27 | 1 | 1 | R-22 | NoTreat | 60 | Apr | Nov | 2
2 | cart barn 1 | 1 | Compressor | 208 | 19.9 | 130 | 3 | 1 | R-22 | 1/4 | 60 | Apr | Nov | 1
3 | cart barn 1 | 1 | Cond.Fan | 208 | 0 | 0 | 1 | 0.24 | N/A | N/A | 60 | Apr | Nov | 0.2
4 | cart barn 4 | 1 | Compressor | 208 | 16 | 125 | 3 | 4.9 | R-22 | NoTreat | 60 | Apr | Nov | 4.9
5 | cart barn4 | 1 | Cond.Fan | 208 | 0 | 0 | 1 | 0.25 | N/A | N/A | 60 | Apr | Nov | 0.3
6 | cart barn 3 | 1 | Compressor | 208 | 14.1 | 105 | 3 | 4.3 | R-22 | NoTreat | 60 | Apr | Nov | 4.3
7 | cart barn 3 | 1 | Cond.Fan | 208 | 0 | 0 | 1 | 0.25 | N/A | N/A | 60 | Apr | Nov | 0.3
8 | cart barn 5 | 1 | Compressor | 208 | 13.46 | 120 | 3 | 4.1 | R-22 | NoTreat | 60 | Apr | Nov | 4.1
9 | cart barn 5 | 1 | Cond.Fan | 208 | 0 | 0 | 1 | 0.75 | N/A | N/A | 60 | Apr | Nov | 0.8
10 | Pro shop 1 | 1 | Compressor | 208 | 13.5 | 99 | 3 | 4.1 | R-22 | NoTreat | 60 | Apr | Nov | 4.1
11 | Pro shop 1 | 1 | Cond.Fan | 208 | 1.4 | 0 | 1 | 0.25 | N/A | N/A | 60 | Apr | Nov | 0.3
12 | pro shop 2 | 1 | Compressor | 208 | 21.5 | 124 | 3 | 6.6 | R-22 | NoTreat | 60 | Apr | Nov | 6.6
13 | pro shop 2 | 1 | Cond.Fan | 208 | 2.7 | 0 | 1 | 0.33 | N/A | N/A | 60 | Apr | Nov | 0.3
14 | pro shop 3 | 1 | Compressor | 208 | 22.8 | 128 | 3 | 7 | R-22 | NoTreat | 60 | Apr | Nov | 7
15 | pro shop 3 | 1 | Cond.Fan | 208 | 3.8 |  | 1 | 0.5 | R-22 | NoTreat | 60 | Apr | Nov | 0.5
16 | club housr roof top 1 | 1 | Compressor | 208 | 19.9 | 130 | 3 | 6.1 | R-22 | NoTreat | 60 | Apr | Nov | 6.1
17 | club house roof top 1 | 1 | Cond.Fan | 208 | 1.6 |  | 1 | 0.3 | N/A | N/A | 60 | Apr | Nov | 0.3
18 | club house roof top 2 | 1 | Compressor | 208 | 19.9 | 130 | 3 | 6.1 | R-22 | NoTreat | 60 | Jan | Dec | 6.1
19 | club house roof top 2 | 1 | Cond.Fan | 208 | 1.4 |  | 1 | 0.2 | N/A | N/A | 60 | Jan | Dec | 0.2
20 | club house roof top 3 | 1 | Compressor | 208 | 17.3 | 123 | 3 | 5.3 | R-22 | NoTreat | 60 | Jan | Dec | 5.3
21 | club house roof top 3 | 1 | Cond.Fan | 208 | 1.4 |  | 1 | 0.2 | R-22 | NoTreat | 60 | Jan | Dec | 0.2
22 | club house roof top 4 | 1 | Cond.Fan | 208 | 1.6 |  | 1 | 0.3 | R-22 | NoTreat | 168 | Apr | Nov | 0.3
23 | Tennis court | 1 | Compressor | 208 | 13.7 | 7.5 | 1 | 2.4 | R-22 | NoTreat | 168 | Apr | Nov | 2.4
24 | tennis court | 1 | Cond.Fan | 208 | 1.4 |  | 1 | 0.25 | R-22 | NoTreat | 168 | Apr | Nov | 0.3
25 | Clubhouse front-left | 1 | Compressor | 208 | 24.4 | 140 | 1 | 4.3 | R-22 | NoTreat | 168 | Apr | Nov | 4.3
26 | Clubhouse front-left | 1 | Cond.Fan | 208 | 1.4 |  | 1 | 0.25 | N/A | N/A | 168 | Apr | Nov | 0.3
27 | club house roof top 4 | 1 | Compressor | 208 | 19.9 | 130 | 3 | 6.1 | R-22 | NoTreat | 60 | Apr | Nov | 6.1
28

## Refrigeration
Refrigeration
[5 empty] | Nameplate Data |  |  |  | Mechanical Data |  | Total |  | Measured Data
No | Location | Qty | Item | Volts | RLA | LRA | Ph | HP | Refrigerant | Line Size | HP | Volts | Amps | KW | KVAR | %THD/I-F
1 | KITCHEN WALKIN FREEZER 1 | 2 | Self-Contained | 208 | 1.1 |  | 1 | 0.2 | R-22 | NoTreat | 0.4
2 | KITCHEN WALKIN FREEZER 2 | 2 | Self-Contained | 115 | 2 |  | 1 | 0.2 | R-22 | NoTreat | 0.4
3 | KITCHEN WALKIN FREEZER 3 | 2 | Self-Contained | 230 | 2 |  | 1 | 0.4 | R-22 | NoTreat | 0.8
4 | MAINTENANCE BLDG ICE MACHINE | 1 | Cond.Fan | 115 | 2 |  | 1 | 0.2 | R-404A | NoTreat | 0.2
5 | MAINTENANCE BLDG ICE MACHINE | 1 | Compressor | 115 | 13 |  | 1 | 1.3 | N/A | N/A | 1.3
6 | MAINTENANCE BLDG SMALL REFRIGERATOR | 2 | Self-Contained | 115 | 0.8 | 5 | 1 | 0.1 | R-134a | NoTreat | 0.2
7 | KITCHEN DISPLAY REFRIGERATOR | 2 | Self-Contained | 120 | 0 |  | 1 | 0.2 | R-134a | NoTreat | 0.4
8 | KITCHEN UPRIGHT FREEZER | 3 | Self-Contained | 115 | 7.5 |  | 1 | 0.3 | R-134a | NoTreat | 0.9
9 | KITCHEN ICE MACHINE | 1 | Self-Contained | 120 | 6 |  | 1 | 1 | R-404A | NoTreat | 1
10 | CART BARN ICE MACHINE | 1 | Self-Contained | 220 | 10.2 | 61 | 1 | 1.9 | R-404A | NoTreat | 1.9
11 | POOL ICE MACHINE | 1 | Compressor | 115 | 5.9 |  | 1 | 0.6 | R-134a | NoTreat | 0.6
12 | POOL ICE MACHINE FAN | 1 | Cond.Fan | 115 | 9.2 |  | 1 | 0.9 | N/A | N/A | 0.9
13 | POOL COKE DISPLAY 6 FT | 1 | Self-Contained | 115 | 7.5 |  | 1 | 0.33 | R-134a | NoTreat | 0.3
14 | POOL COKE DISPLAY SMALL | 1 | Self-Contained | 115 | 0 |  | 1 | 0 | R-134a | NoTreat | 0
15 | TENNIS ICE MACHINE | 1 | Self-Contained | 120 | 6 |  | 1 | 0.6 | N/A | NoTreat | 0.6
16

## Incandescent
Incandescent Lights
No | Location | Fix. Qty. | Type | Bulb/Fix. | Bulb Watt | Month | Circuit | H\W
1 | TL 5 CONFERENCE ROOM | 3 | Std | 3 | 75 | 12 | Clean | 50
2 | TL 5 CONFERENCE ROOM | 1 | Spot | 3 | 50 | 12 | Clean | 50
3 | TL 5 WALKWAY | 4 | Flood | 1 | 65 | 12 | Clean | 50
4 | TL 5 WALKWAY-EMERGENCY UNIT | 2 | Flood | 2 | 5.4 | 12 | Clean | 0
5 | GF FOYER | 2 | Std | 1 | 40 | 12 | Clean | 50
6 | GF FOYER-EXIT | 2 | Std | 2 | 18 | 12 | Clean | 50
7 | GF FOYER | 4 | Std | 5 | 40 | 12 | Clean | 50
8 | GF FOYER | 5 | Flood | 1 | 65 | 12 | Clean | 50
9 | GF FOYER-CHANDELIER | 2 | Std | 30 | 40 | 12 | Clean | 50
10 | GF FOYER-OFFICE 1 CEILING FAN | 1 | Std | 4 | 75 | 12 | Clean | 50
11 | GF FOYER-OFFICE 2 CEILING FAN | 1 | Std | 4 | 75 | 12 | Clean | 50
12 | GF FOYER-OFFICE 3 CEILING FAN | 1 | Std | 4 | 75 | 12 | Clean | 50
13 | GF HALL | 7 | Flood | 1 | 65 | 12 | Clean | 50
14 | GF SERVICE HALL | 2 | Flood | 1 | 65 | 12 | Clean | 50
15 | GF ELECTRIC PANEL ROOM | 1 | Std | 1 | 75 | 12 | Clean | 50
16 | GF HALL EMERGENCY | 1 | Std | 2 | 5.4 | 12 | Clean | 0
17 | GF STAIRS TO BASEMENT | 3 | Flood | 1 | 75 | 12 | Clean | 50
18 | GF SERVICE AREA | 9 | Flood | 1 | 75 | 12 | Clean | 50
19 | CLUB HOUSE OUTSIDE DAYLIGHT SENSORED | 5 | Flood | 1 | 150 | 12 | Clean | 84
20 | GF FREEZER/COOLER KITCHEN | 3 | Std | 1 | 60 | 12 | Clean | 50
21 | GF1 DINING | 30 | Flood | 1 | 75 | 12 | Clean | 50
22 | GF1 DINING-CHANDELIER | 2 | Std | 15 | 40 | 12 | Clean | 50
23 | GF1 DINING-EXIT | 1 | Std | 2 | 18 | 12 | Clean | 50
24 | GF MEN'S ROOM | 6 | Flood | 1 | 75 | 12 | Clean | 50
25 | GF MEN'S ROOM | 2 | Std | 1 | 60 | 12 | Clean | 50
26 | GF HALL BY BATHROOMS | 5 | Flood | 1 | 75 | 12 | Clean | 50
27 | GF LADIES LOUNGE | 5 | Flood | 1 | 75 | 12 | Clean | 50
28 | GF LADIES LOUNGE | 2 | Std | 1 | 60 | 12 | Clean | 50
29 | GF2 DINING | 15 | Flood | 1 | 75 | 12 | Clean | 50
30 | GF3 DINING | 19 | Flood | 1 | 75 | 12 | Clean | 50
31 | GF BAR AREA | 18 | Flood | 1 | 75 | 12 | Clean | 50
32 | GF BAR AREA | 2 | Spot | 1 | 50 | 12 | Clean | 50
33 | B PRO SHOP | 11 | Spot | 3 | 50 | 12 | Clean | 50
34 | B PRO SHOP-EXIT | 1 | Std | 2 | 18 | 12 | Clean | 50
35 | B PRO SHOP-SPOTLIGHTS IN FURNITURE | 7 | Std | 3 | 50 | 12 | Clean | 50
36 | B TELEPHONE/PANEL | 1 | Flood | 1 | 75 | 12 | Clean | 50
37 | B HALL-EXIT | 2 | Std | 2 | 18 | 12 | Clean | 50
38 | B LADIES ROOM | 5 | Flood | 1 | 65 | 12 | Clean | 50
39 | B LADIES ROOM | 2 | Std | 1 | 75 | 12 | Clean | 50
40 | B MEN'S LOCKER BATHROOM | 11 | Flood | 1 | 65 | 12 | Clean | 50
41 | B LADIES ROOMB-MENS LOCKER EXIT | 2 | Std | 2 | 18 | 12 | Clean | 50
42 | B MEN'S LOCKER BATHROOM | 2 | Std | 1 | 75 | 12 | Clean | 50
43 | B FITNESS CENTER-EXIT | 1 | Std | 2 | 18 | 12 | Clean | 50
44 | B PRO SHOP-EXIT | 1 | Std | 2 | 18 | 12 | Clean | 50
45 | B PORCH CEILING FAN | 4 | Std | 3 | 60 | 12 | Clean | 50
46 | MAIN CLUB HOUSE OUTSIDE ENTRANCE | 3 | Std | 3 | 40 | 12 | Clean | 50
47 | GF BALCONY IN FRONT OF DINING | 2 | Flood | 2 | 65 | 12 | Clean | 50
48 | GF BALCONY IN FRONT OF DINING | 4 | Std | 3 | 75 | 12 | Clean | 50
49 | GF BALCONY IN FRONT OF DINING-CEILING FAN | 1 | Std | 2 | 75 | 12 | Clean | 50
50 | MAINTENANCE BLDG | 4 | Flood | 2 | 65 | 12 | Clean | 50
51 | EXIT SIGN-CART BARN | 1 | Std | 2 | 18 | 12 | Clean | 50
52 | POOL CEILING FANS | 4 | Std | 3 | 60 | 12 | Clean | 50
53 | POOL ROOM DECORATIVE | 3 | Std | 3 | 50 | 12 | Clean | 50
54 | POOL ROOM FLOOD LIGHTS | 32 | Flood | 1 | 65 | 8 | Clean | 50
55 | TENNIS SHOP | 3 | Flood | 2 | 65 | 8 | Clean | 50
56 | TENNIS SHOP | 7 | Flood | 3 | 75 | 8 | Clean | 50
57 | TENNIS SHOP | 1 | Flood | 4 | 75 | 8 | Clean | 50
58 | TENNIS SHOP BATHROOMS | 4 | Std | 3 | 75 | 8 | Clean | 50
59 | TENNIS COURT HUT CEILING FAN | 1 | Std | 2 | 60 | 12 | Clean | 50
60
61
62
63
64

## HID
HID Lights
No. | Location | Fix. Qty | Type | Bulbs Per Fixture | Bulb Watts | Breaker | Ballast Type | Volts | Months | H/W
1 | TENNIS COURTS STADIUM | 4 | MH | 3 | 1000 | Panel | AutoTransformer | 240 | 8 | 26
2 | OTHER TENNIS COURTS SINGLE FIXTURE | 12 | MH | 1 | 1000 | Panel | AutoTransformer | 240 | 8 | 26
3 | OTHER TENNIS COURTS SINGLE FIXTURE | 12 | MH | 2 | 1000 | Panel | AutoTransformer | 240 | 8 | 26
4