PowerLiner™

Distortion Power Correction System

# Installation Guidelines

- Fix the PowerLiner to its final installation location by means of the holes supplied in the Unit’s flanges with anchor bolts or studs and nuts.

- Install PowerLiner’s electrical connections on the Line Side of the Non-Linear Load. Non Linear loads such as AC and DC Variable Speed Drives, Arc Furnaces, Welders, Rectifiers, etc.

WARNING: Never install a PowerLiner on the Load Side of any Variable Speed Drive, Soft-Start Starter, or any solid state device that drives a Non-Linear Load.

- Make sure the load is switched off at its service disconnect. Install the wires feeding the PowerLiner following N.E.C. guidelines and/or local codes. Size wires to 135% of the PowerLiner’s Nameplate Amps. Should fusing be required as per N.E.C. Article 460, you must supply an external fuse block and fuses. If time-delay fuses are used, the fuse rating should be between 150% and 175% of Nameplate Amps. If fast-acting fuses are used, the fuse rating should be between 250% and 300% of Nameplate Amps.

- Clean the interior of the PowerLiner enclosure and make sure no scrap wire or metal debris is loose inside. Make a final visual inspection and verify that all the connections are firmly tightened and that there is a secure ground connection.

- Apply power to the Treated Load. Load should work as usual.